## Slide 1
Lab 1
Lab 2
Lab 3
Lightning
Spike
Motor
Surge Voltage
Sag Voltage
Power flow diagram from Generating Station to Wall socket

## Slide 2
Power
Disturbances
Voltage Sag
Wave form
Effects on Computer System
Loss of Data,
Shut down,
Restart of a system
Voltage Surge
Common power problems
Tripping of system,
System damage,
System life reduced
Voltage Spike
Loss of data,
System damage,
System life reduced

## Slide 3
Power
Disturbances
Blackout
Wave form
Effects on Computer System
Loss of Data,
Shut down
Brownout
Common power problems
Tripping of system,
System Shutdown,
System life reduced
Harmonics
Loss of data,
Over heating system
System life reduced

## Slide 4
UPS
UNINTERRUPTIBLE POWER SUPPLY

## Slide 5
An uninterruptible power supply, UPS is an electrical apparatus that provides emergency power to a load when the input power source fails. It provides instantaneous protection from input power interruptions by means of one or more attached batteries and associated electronic circuitry.
UNINTERRUPTIBLE POWER SUPPLY

## Slide 6
Types of UPS
Offline UPS
Line Interactive UPS
Online UPS

## Slide 7
Off Line UPS

## Slide 8
Off Line UPS

## Slide 9
Line Interactive UPS

## Slide 10
Normal Condition
Line Interactive UPS

## Slide 11
Over voltage Condition
Line Interactive UPS

## Slide 12
Under voltage Condition
Line Interactive UPS

## Slide 13
Blackout Condition
Line Interactive UPS

## Slide 14
On Line UPS
AC
AC
AC
AC
DC
DC
AC
Battery
Q1 (I/P)
Q2 (Bypass)
Q3 (Maintenance Bypass)
Q4 (O/P Switch)
Transfer
Switch
I/P
O/P
Rectifier /
Charger
Inverter

## Slide 15
Step 1: Add up the nameplate power of the anticipated loads.
Step 2: Multiply the anticipated VA number by 0.9 to estimate the actual power, in watts, that the critical load will represent.
Step 3: Divide the number by 1,000 to establish the kilowatt (kW) load level of the anticipated critical load.
UPS load Calculation
Server | VDI Servers : Boston x86 Server SuperChassis 825TQ-R740LPB
Quantity | 22 Nos
Maximum Power Consumed by each node | 740 Watts
Total Power Consumed (Max) | 16.28 Kwatts
Power Facor of server Power Supply | 0.9
Load to UPS (Max) | 18 KVA
Example:

## Slide 16
Backup time Calculation
Battery Voltage | Capacity (AH) | No of Batteries | Battery Bank Voltage | Efficiency of UPS | Load (KW) | Backup Time
12 V | 200 | 34 | 12 X 34 = 408V | 80 % | 80 KW | 0.8 Hours = 49 Minutes
Backup time = (12v * 200AH * 34 * 0.8)/80,000W
= 0.816 Hours or 49 Minutes
Backup Time = (Battery Vtg * AH * No of Batteries * Efficiency)/Load in Watts

## Slide 17
Emerson
20 KVA
I/P 415V ~
O/P 230 V~
Input Panel – 1
Class IV
Power Distribution Layout at Computer Division (Ground Floor)
Input Panel – 2
Class III (DG Backup)
I/P UPS 4
3 Φ 415 V ~
From Sub Station
DB
Output of UPS4
Rack 2 (EID servers)
Bull Nova Master Node
Rack 3 (Everrun server)
Rack 4 (SMP servers)
DAE Grid
I/O room peripherals
Emerson
20 KVA
I/P 415V ~
O/P 230 V~
Emerson
20 KVA
I/P 415V ~
O/P 230 V~
Int.& Email
Emerson
20 KVA
I/P 415V ~
O/P 230 V~
I/P UPS 2
I/P UPS 3
I/P UPS 5
DB - 1
DB - 2
DB
Output of UPS1
OLAP, DFIS, APAR
HPC Fire, PVelite
Xeon Server1 & 2
Workstations
I/O Room (spare)
HPC Network Rack
VDI Servers Rack
DB
Output of UPS4
Rack 1
(OPA,lic,FW,LDAP)
Rack 2
(EID servers)
Rack 4
(SMP servers)
VDI Servers Rack
Internet Setup
Email Server
Anunet Setup
Web Servers
UPS-1 - 5KVA
UPS-2 - 4KVA
UPS-3 - 7KVA
UPS-4 - 4.3KVA
UPS-5 - 6KVA
Load Details
Emerson
20 KVA
I/P 415V ~
O/P 230 V~
Disaster Recovery
I/P UPS 1
VDI Servers Rack
Emerson
30 KVA
I/P 415V ~
O/P 415V~
Worktation
DB
at Backbone
Room
CORE Switch
Workstation
I/P UPS

## Slide 18
COMPUTER CENTRE ANNEX FLOOR II PCC
1600A TP ACB CLASS IV
SERVER DISTRIBUTION PANEL – 1
400A TPN SFU
SERVER DISTRIBUTION PANEL – 2
400A TPN SFU
MCB1 63A 4P
MCB2 63A 4P
MCB3 63A 4P
MCB4 63A 4P
MCB5 63A 4P
MCB6 63A 4P
MCB7 63A 4P
MCB8 63A 4P
MCB9 63A 4P
MCB10 63A 4P
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
UPS 4
SPARE
RACK 10
RACK 11
RACK 12
RACK 13
RACK 14
RACK 15
RACK 16
FLDB 4*2P 32A
RACK 9
MCB1 63A 4P
MCB2 63A 4P
MCB3 63A 4P
MCB4 63A 4P
MCB5 63A 4P
MCB6 63A 4P
MCB7 63A 4P
MCB8 63A 4P
MCB9 63A 4P
MCB10 63A 4P
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
FLDB 4*2P 32A
SPARE
SPARE
UPS 3
SPARE
RACK 2
RACK 3 SPARE
RACK 6
RACK 7
RACK 8
Head, Management
Console Monitors
FLDB 4*2P 32A
RACK 4
RACK 1,TEST RACK
IVY CLUSTER POWER DISTRIBUTION LAYOUT
RACK 9
FLDB 4*2P 32A
FLDB 4*2P 32A
RACK 5

## Slide 19
INCOMER FROM PCC ROOM
CLASS III PANEL
VDB 1
125A 4P MCB
UPS 1
UPS 2
FLDB 4*2P 32A
FLDB 4*2P 32A
RACK 5
RACK 3
RACK 4
KMS RACK
UPS-1 - 2.3KVA
UPS-2 - 6.3KVA
UPS-3 - 6.6KVA
UPS-4 - 3.2KVA
Load Details
Rack 5
Head 1
MDS1,2
OSS1,2,3,4
Rack 3
Pie nodes
Compute nodes
Rack 4
Head 2
IB Switch
Rack 9
Management
Tape Library

## Slide 20
Network
Annex building
1st floor
Annex building
Ground floor
Operator sitting area
20KVA UPS’s
120 KVA UPS’s
1
2
3
4
1
2
Remote Monitoring of UPS

## Slide 21
Remote Monitoring of UPS
Normal operation of UPS.

## Slide 22
UPS in bypass mode.
Remote Monitoring of UPS

## Slide 24
Thank you