## UPS Status
IVY Cluster UPS
UPS Name | Capacity | UPS installed on | Class | Input | Output | Connected Load | DC BUS | Charge Amps | Battery Bank volt | VRLA Battery Details | Battery Replaced on | Location | Present Condition
UPS1 | 20KVA | 2015-05-01 | III | 387V,11A | 229V,30A-8.2KW/7.1KVA | IB,Rack 6 (nodes 97-136), Head -2,mds1-2,oss1-4&Certification Authority Room | 353V-FLOAT | 0.75A | 356V | 26-nos, 12V, 42Ah, 14KG | 2019-07-25 | IVY Battery Room | Good
UPS2 | 20KVA | 2015-05-01 | III | 391V,17A | 228V,48A-12.3KW/11.2KVA | IB, HEAD 1, Head-2,Rack 6 (nodes 97-136), Back bone Network Switch | 350V-FLOAT | 1.12A | 354V | 26-nos, 12V, 42Ah, 14KG | 2018-10-09 | IVY Battery Room | Good
UPS3 | 20KVA | 2015-07-01 | IV | 425V,1A | 230V,0.1A- 0.1KW/0.0KVA | IPDU-9(HEAD 1) | 352V-FLOAT | 0.12A | 357V | 26-nos, 12V, 42Ah, 14KG | 2019-02-01 | IVY Battery Room | Rectifier Antisat Trip
UPS4 | 20KVA | 2015-07-01 | IV | 415V,12A | 233V,31A-6.9KW/7.1KVA | Management node, tape library, node177-200,KMS1-2 | 352V-FLOAT | 0.87A | 352V | 26-nos, 12V, 42Ah, 14KG | 2019-02-01 | IVY Battery Room | Good
Ground Floor UPS Status
UPS Name | Capacity | UPS installed on | Class | Input | Output | Connected Load | DC BUS | Charge Amps | Battery Bank volt | VRLS Battery Details | Battery Replaced on | Location | Working Condition
UPS1 | 20KVA | 2008-11-01 | III | 387V,10A | 230V,25A-5.3KW/5.7KVA | VDI Servers | 359V-FLOAT | 0.75A | 360V | 26-nos, 12V, 42Ah, 14KG | 2016-07-27 | I/O Room | Good
UPS2 | 20KVA | 2008-11-01 | III | 391V,13A | 230V,34A-7.3KW/7.8KVA | HPC Server room, workstation | 363V-FLOAT | 1.0A | 364V | 26-nos, 12V, 42Ah, 14KG | 2017-06-16 | I/O Room | Good
UPS3 | 20KVA | 2007-05-01 | III | 415V | 230V | Anunet & Internet servers |  |  | 364V | 26-nos, 12V, 42Ah, 14KG | 2017-10-15 | I/O Room | Good
UPS4 | 20KVA | 2007-05-01 | IV | 409V,7A | 230V,21A-4.6KW/4.8KVA | HPC Server room, bullnova, everrun server, HBNI & WINLS | 360V-FLOAT | 0.37A | 360V | 26-nos, 12V, 42Ah, 14KG | 2018-10-09 | I/O Room | Good
UPS5 | 20KVA | 2013-04-01 | III | 385V,11A | 229V,28A-5.8KW/6.4KVA | Backbone & disaster recovery storage | 350V-FLOAT | 0.62A | 350V | 26-nos, 12V, 42Ah, 14KG | 2019-07-25 | I/O Room | SMPS Not OK
UPS6 | 20KVA | 2013-04-01 | IV | 395V,8A | 229V,20A-4.1KW/4.5KVA | VDI Servers&Backbone Core switch | 353V-FLOAT | 0.87A | 355V | 26-nos, 12V, 42Ah, 14KG | 2018-10-09 | I/O Room | Good
LAB UPS | 10KVA |  | IV | 243V | 240V,2A | Network Lab | [5 empty] | I/O Room | Good
UPS1 | 120KVA | 2009-10-01 | IV | 407V, R-29.9A, Y-45.3A, B-44.4A | 389V, R-32A, Y-28A, B-26A, 19.78KVA | NEHA Cluster |  |  | 452V | 34-nos, 12V, 200Ah, 67.2KG | 2019-04-12 | Annex buiding UPS Room | Good
UPS2 | 120KVA | 2009-10-01 | IV | 407V, R-28.9A, Y-28.2A, B-27.7A | 399V, R-12A, Y-11A, B-13A, 8.28KVA | Xeon Cluster |  |  | 452V | 34-nos, 12V, 200Ah, 67.2KG | 2019-04-12 | Annex buiding UPS Room | Good

## Load details
Name of the UPS | input in KVA | Load in KVA | UPS capaity in KVA | Load in % | UPS efficiency
IVY-UPS1 | 8.1 | 7.1 | 20 | 35.5 | 87.6543
IVY-UPS2 | 12.3 | 11.2 | 20 | 56 | 91.0569
IVY-UPS3 | 0.7 | 0.1 | 20 | 0.5 | 14.2857
IVY-UPS4 | 8.6 | 7.1 | 20 | 35.5 | 82.5581
I/O-UPS1 | 6.7 | 5.7 | 20 | 28.5 | 85.0746
I/O-UPS2 | 8.8 | 7.8 | 20 | 39 | 88.6364
I/O-UPS3 |  |  | 20 | 0 | #DIV/0!
I/O-UPS4 | 4.95 | 4.8 | 20 | 24 | 96.9697
I/O-UPS5 | 7.33 | 6.41 | 20 | 32.05 | 87.4488
I/O-UPS6 | 5.5 | 4.6 | 20 | 23 | 83.6364
I/O-LAB UPS |  |  | 5 | 0 | #DIV/0!
CLUSTER-UPS1 | 27.5 | 19.78 | 120 | 16.4833 | 71.9273
CLUSTER-UPS2 | 19.5 | 8.28 | 120 | 6.9 | 42.4615
TOTAL | 109.98 | 82.87 | 445 | 18.6225 | 75.3501